## A1 - System Layout
New Riser
|  |  | Stairwell #2 |  |  |  | 2" EMT- 18x18x4 can |  |  | Main Stairwell #1
Penthouse to 2nd floor
|  |  |  | Roof Top |  | 1" EMT conduit |  |  |  | Central plant PENTHOUSE
|  |  |  | 12 |  |  |  | Electrical/IDF Rm's |  |  | 12
|  |  |  | 11 | [6 empty] | 11 |  | PNL#5 | PNL#6 | PNL #5&6 Floors 11,12 & penthouse
|  |  |  | 10 | [6 empty] | 10 |  | PNL#5 Floors 10,9 &8
|  |  |  | 9 | [6 empty] | 9
|  |  |  | 8 | [6 empty] | 8
|  |  |  | 7 | [6 empty] | 7 |  | PNL #4
|  |  |  | 6 | [6 empty] | 6 |  | PNL#4 Floors 7,6 &5
|  |  |  | 5 | [6 empty] | 5
(2) doors: patio and stairwell |  |  |  | 4 |  |  |  | 3 |  |  | 4 |  | PNL#3 | PNL#2 Floors 4,3 &2
|  | Stairwell #3 |  | 3 | [6 empty] | 3 | patio door
| patio door | Hallway |  | 2 | Jbx |  |  |  |  | Jbx | 2 |  | PNL #2
|  | 1 | [6 empty] | Elevators |  | 1 |  | PNL #1,2- Floors 1,P-1 &P-2 roll up door and puch button
|  | P-1 | Parking elevator |  | Guard station |  | turnstiles |  |  |  | P-1 | Garage |  | Parking rollup gate
|  | P-2 | [8 empty] | P-2 | Garage
ZOOM IN LOBBY
6#
#2#2
33
Fire pnl Rm
#4
#2
#3
#5
#6
#1
PNL # 1
18x18 x4 Cans
PNL #1&2 mounted on 2nd floor

## A2 - Zoom in Lobby
PNL 1&2 mounted on 2nd floor- Elec Rm
|  | Stairwell two |  |  |  |  | 1" EMT conduit |  | Stairwell one
|  | Second floor stairwell | [6 empty] | Second floor stairwell
Electronic Hardware)Schedule hours-timmer | Patio Door |  |  | Guard station | Turnstiles | Elevators |  | 2nd Fl Elec Rm /IDF |  | Patio Door | Electronic Hardware)Schedule hours-timmer
Street level | Stairwell three | [6 empty] | Lobby 1st floor |  |  | Fire panel room first floor & Elevator monitor & selector switch | Two 1" EMT | print E2 - B
| P-1 Garage |  | 1" EMT conduits |  |  | Garage |  |  |  |  | P-1 PARKING. EBL panel. Electrical room. Main phone board & Data riser two 2nd floor Details on print E2 - B
| P-2 Garage |  |  |  |  | Garage
Electronic Hardware)Schedule hours-timmer
Lobby
Elec Rm
14 St Exit
Data / Phone gutter Gutter P-1 Garage to 2nd fl Data
Roll up Door and Push botton
Garage

## A3 -Typical conduit path
Typical conduit path and layout for each floor. 12th floor through 2nd floor
1" EMT
|  |  |  | 18X18X4" Pull can |  | Picture #1
2" EMT
[6 empty] | 12th floor electrical/ IDF room | 2" EMT riser conduit penthouse to 2nd floor electrical room
**Typical conduit paths on each floor. 12th floor through 2nd floor |  |  | ELEC /IDF Rm to card reader to stairwells 1&2
IDF (Intermediate Distribution Frame) Room- Secondary voice/data network location
Typical conduit path for card readers at each floor. 12th floor through 2nd floor
Conduit path Pictures #1 to #4 to #3 to #2
Blue line on floor plan
Picture #2
1inch conduit path to a new card reader Inside stairwell
Start at picture #3 to #2
Second junction box for card reader system. 1 inch conduit mounted and ran along wall to I beam.
Mount a box on wall before transitioning into wall cavity. Pull wire down wall into junction box for new card reader.
This is typical for floors 12 through 2nd floor. Card readers to be installed at 42.5" inches center at finish floor
| Stairwell number two #2 | Stairwell number one #1
| T bar celing |  |  |  |  | Picture #3
| Install 1 inch conduit from electrical /IDF room. |  |  |  |  | Two junction box to be mounted one card reader one with a pull string future camera system.
Set 1 junction box after leaving electrical rm and before penetrating stairwell #2 wall
| Pull cabled to new card reader junction box installed at 42.5" center AFF inside stairwell # 2. cable inside wall. |  |  |  |  | Start at picture #4 to #3
No exposed conduit below T-bar celing
Picture #4
1 inch conduit with pull string paralleled to conduit. path above celing
From electric rooms 18x18 can, to inside of stairwell Pictures 1 &3

## A4 - Basement & Lobby
Panel EBL1 find 4 FOUR circuits one spare two for security guard station one for turnstiles.
Available circuits 15,16,18&20
Approx location of Main Fire Panel -
Room 1st floor lobby.
Approx location of security station 1st floor lobby
MFP
Panel EBL1 find 4 FOUR circuits one spare two for security guard station one for turnstiles.
Available circuits 15,16,18&20
Approx location of Main Fire Panel -
Room 1st floor lobby.
Approx location of security station 1st floor lobby
MFP
Picture #1
Picture #2
Picture #2
Picture #3
Picture #4

## A5 - Device Locations
All card reader to be installed at 42.5" inches center at finish floor.
|  | Stairwell One & Two (#1&2 ) |  | Stairwell Three (#3)
| Stairwell # |  |  |  | Stairwell #
Penthouse/roof | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF | FLOOR #2-Outside Patio | by #2,3 | Card reader to be installed at 42.5 inches center at finish floor inside and outside of door.
FLOOR #12 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF | FLOOR #2- MAIN DOOR | #3 | Has existing panic bar Outside stairwell. Install Card reader inside stairwell. At 42.5"@ center
FLOOR #11 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF | FLOOR #1- MAIN DOOR- 14. st exit | #3 | Outside of stairwell Card reader to be installed at 42.5 inches at finish floor
FLOOR #10 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF | Parking garage P1 | #3 | Inside Stairwell Card reader to be installed at 42.5 inches at finish floor
FLOOR #9 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF | Parking garage P2 | #3 | Inside Stairwell Card reader to be installed at 42.5 inches at finish floor
FLOOR #8 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #7 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #6 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #5 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #4 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #3 | # 1&2 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #2 | #1 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | 42.5" @AFF
FLOOR #2-Outside Patio | #1 side | Card reader to be installed at 42.5 inches center at finish floor inside and outside of door.
FLOOR #2 | #2 | Card reader to be installed at 42.5 inches center at finish floor-NOTE Outside of stairwell #2 | 42.5" @AFF
FLOOR #1 | #1 | Card reader to be installed at 42.5 inches center at finish floor-NOTE Outside of stairwell #1 | 42.5" @AFF
Parking garage P1 | #1 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | Top of door
Parking garage P2 | #1 | Inside Stairwell Card reader to be installed at 42.5" inches center at finish floor | Top of door
Location of new AMAG cabinets.
**With a minimum of eight node controllers.
Electrical/IDF Rm | FLOOR # 11 | (2 Ea) | Pnl 5 ,6
Electrical/IDF Rm | FLOOR # 7 | (1 Ea) | Pnl 4
Electrical/IDF Rm | FLOOR # 4 | (1 Ea) | Pnl 3
Electrical/IDF Rm | FLOOR # 2 | (2 Ea) | Pnl 1, 2

## A6 - Station
Entrance door to be Modified
Match south entrance door ADA compliance
** Glazing on Security Station
lobby stanchion's /delineator
https://crowdcontrolcompany.com/prod/retractable-belt-stanchions/
Fastlane Glassgate 150 – Speedgate Turnstile ¦ Integrated Design Limited (fastlane-turnstiles.com)
Turnstiles
MIRROR

## A7 - Door Hardware
Key in Lever locks.
Lever lock Part # ND 80 PD Rho 613 RX. Rex in handle. E keyway.
https://us.allegion.com/content/dam/allegion-us-2/webdocuments-2/Catalog/Schlage_ND_Series_Catalog_106501.pdf
Mortise locks Part # EL/EU 9092 P 06B RX 613 E keyway cylinder.
https://us.allegion.com/content/dam/allegion-us-2/webdocuments-2/Catalog/Schlage_L_Series_Catalog_102899.pdf
Doors with Von Duprin hardware Part # E 996L 06 613 with REX in bar 050251 switch kit.
https://us.allegion.com/content/dam/allegion-us-2/webdocuments-2/DataSheet/Von_Duprin_E996L_Electrified_Breakaway_Lever_Trim_Data_Sheet_110103.pdf
Closers (if needed) Part # LCN 4040 XP 613.
https://www.allegion.ca/en/home/products/categories/doorcontrol/lcn-4040xp.html
Note the REX or request to exit is in the handle/locks.